## 10KW
Material Purchase Specification
(High Frequency DC Power Supply for ESP)
Project Name |  | : | 동서식품 부평공장 |  |  |  |  | 담당
Customer |  | : | 피에스솔루텍 |  | EPC | E-Gen |  | 연락처
Order Quantity |  | : |  | Set | 1 |  |  | E-mail
Delivery |  | : | 2021 | Oct | 29
Design Specifications
1. General Rating | [8 empty] | Remark
1.1 | Enclosure | : | Outdoor
1.2 | Ambient Temp | : | Minimum | -20 | ℃ | Maximum | 40 | ℃
1.3 | Humudity | : | Maximum | 100 | %
1.4 | Altitude | : | Lower than | 1000 | Meter
1.5 | Cooling Method | : | ONAN
1.6 | Protection | : | IP56
1.7 | Insulation Oil | : | Mineral Oil
1.8 | Certificate | : | None | None | None
적용기준
2. Electrical Specifications | [10 empty] | 10kW급 | 20kW 이상
2.1 | Input Voltage | : | 440 | V | Variation | ±10% | Frequency | 60Hz |  | 효율 | 0.85 | 0.92
2.2 | Input Current | : | 17.3331 | A | [5 empty] | 역률 | 0.9 | 0.93
2.3 | Max. Output Voltage | : | 50 | kV |  |  | Min Vo
2.4 | Max. Output Current | : | 200 | mA |  |  | Min Io
2.5 | Output kW | : | 10 | kW | kVA: | 13.0719
2.6 | MCCB kA (IAC) | : | 25 | kA
2.7 | Efficiency | : | 85 | %
2.8 | EMC Filter | : | None
3. Physical Specifications
3.1 | HV Bushing Type | : | Top | Mounted
3.2 | Ground Switch | : | None | Flange Hole Size | None | Hole Q'ty | None |  | 사각보호박스 필요하고 고압케이블 연결용 커플링 필요합니다
|  |  | Flange Vertical Center Line |  | None |  |  |  | (에너콘스 세호 프로젝트처럼)
3.3 | Key Interlock | : | None | None
3.4 | Radiator | : | Welded On
3.5 | Wheel (Roller) | : | Base Only
3.6 | Pressure Protection | : | Relief Valve
3.7 | Ground Boss | : | Plate
3.8 | Material of Body | : | SS275 | Tank | 3.2t
|  |  |  | Junction Box+Door | 2.0t
|  |  |  | HV Flange | 6.0t
|  |  |  | Base | 4.5t
|  |  |  | HV Bushing Cover | 6.0t | 제조사
3.9 | Painting Type | : | Powder Coat | Thickness | 120 | ㎛
| Color of Paint | : | 5Y 7/1 | 제조사KCC |  | or User Standard
3.10 | Running Light | : | Pilot Lamp on Jbox
3.11 | Drain Valve Size | : | 1/2"
3.12 | Oil Drip Pan | : | None
3.13 | Remote | : | None
3.14 | Remark | : | 키패드는 Junction Box 커버에 부착(2중 도어로 제작)
4. Signal Specifications
4.1 | Digital Input | : | HV On/Off | Remote Ready |  | kV & mA에 대한 4-20mA 신호출력
4.2 | Digital Output | : | HV On | Fault
4.3 | Aux.Alarm | : | Emergency Stop
Aux1
Aux2
Aux3
Aux4
4.4 | Comm.Protocol | : | ModBus RTU
4.5 | Redundant System | : | None