## COVER
Technical Document
|  | PROJECT | : | 10kw 집진기
|  | CUSTOMER | :
|  | DOC. Name | : | 10kw 집진기 Interface List
E | FOR CONSTRUCTION |  |  |  | J.H.KIM |  |  | 2019.05.22
D | FOR CONSTRUCTION |  |  |  | J.H.KIM |  |  | 2019.02.11
C | FOR CONSTRUCTION |  |  |  | J.H.KIM |  |  | 2018.09.12
B | FOR CONSTRUCTION |  |  |  | J.H.KIM |  |  | 2018.02.19
A | FOR CONSTRUCTION |  |  |  | J.H.KIM |  |  | 2018.01.08
REV NO | DESCRIPTION |  |  |  | PREPARED | REVIEWED | APPROVED | DATE
10kw 집진기Interface List

## PROTOCOL(SYNC)
Technical Document
| PROJECT | 10kw 집진기
CUSTOMER
| DOC. Name | 10kw 집진기 Interface List
MODBUS COMMUNICATION PROTOCOL
-. 통신 셋업 : 38400BPS, 8 data bit, No Parity, 1 Stop Bit
Function3 : Read Holding Registers.
Function4 : Read Input Registers.
Function6 : Write Single Register.
Function16 : Write multiple Registers.
1) Function 03(0x03) : 읽기 명령 - Power Supply -> Customer
ex) 0번지부터 2개의 값을 읽자
| Slave address | Function code(03) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo | CRC Lo | CRC Hi
Query : | 0x01 | 0x03 | 0x00 | 0x00 | 0x00 | 0x02 | 0x?? | 0x??
| Slave address | Function code(03) | Byte Count | Data 1 Hi | Data 1 Lo | Data n Hi | Data n Lo | CRC Lo | CRC Hi
Response : | 0x01 | 0x03 | 0x04 | 0x06 | 0x0E | 0x02 | 0xEE | 0x?? | 0x??
2) Function 04(0x04) : 복수 읽기 명령 - Power Supply -> Customer
ex) 0번지부터 2개의 값을 읽자 |  |  |  | `
Query : | Slave address | Function code(04) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo | CRC Lo | CRC Hi
| 0x01 | 0x04 | 0x00 | 0x00 | 0x00 | 0x02 | 0x?? | 0x??
Response : | Slave address | Function code(04) | Byte Count | Data 1 Hi | Data 1 Lo | Data n Hi | Data n Lo | CRC Lo | CRC Hi
| 0x01 | 0x04 | 0x04 | 0x06 | 0x0E | 0x02 | 0xEE | 0x?? | 0x??
3) Function 6(0x06) : 하나 쓰기 명령 - Customer -> Power Supply
ex) 0번지에 00 03(hex) 값을 쓰자
Query : | Slave address | Function code(06) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo | CRC Lo | CRC Hi
| 0x01 | 0x06 | 0x00 | 0x00 | 0x00 | 0x03 | 0x?? | 0x??
Response : | Slave address | Function code(06) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo | CRC Lo | CRC Hi
| 0x01 | 0x06 | 0x00 | 0x00 | 0x00 | 0x03 | 0x?? | 0x??
4) Function 16(0x10) : 복수 쓰기 명령 - Customer -> Power Supply
ex) 0번지부터 2개의 값을 쓰자
Query : | Slave address | Function code(16) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo
| 0x01 | 0x10 | 0x00 | 0x00 | 0x00 | 0x02
|  | Byte Count | Data 1 Hi | Data 1 Lo | Data n Hi | Data n Lo | CRC Lo | CRC Hi
|  | 0x04 | 0x06 | 0x0F | 0x02 | 0xEF | 0x?? | 0x??
Response : | Slave address | Function code(16) | Starting Address Hi | Starting Address Lo | No. of Register Hi | No. of Register Lo | CRC Lo | CRC Hi
| 0x01 | 0x10 | 0x00 | 0x00 | 0x00 | 0x02 | 0x?? | 0x??

## 인터페이스 회로
Technical Document
| PROJECT | 10kw 집진기
CUSTOMER
| DOC. Name | 10kw 집진기 Interface List
-. 인터페이스 회로
○ 신호의 설명
| TX+ | RS485의 송수신(+)신호 또는 RS422의 송신(+)신호
| TX- | RS485의 송수신(-)신호 또는 RS422의 송신(-)신호
| RX+ | RS422의 수신(+)신호
| RX- | RS422의 수신(-)신호
| 공통설명 | 38400bps, 8bit, no parity, 1stop
*. RS485/RS422 2개의 기능 중 1개의 기능만 선택 가능하다. 즉 2개의 채널을 동시에 열 수 없습니다.
-. 커넥터 연결

## PS->Customer(Bit)
Technical Document
PROJECT : 10kw 집진기
CUSTOMER :
DOC. Name : 10kw 집진기 Interface List
Power Supply / Customer COMMUNICATION DATA
| <BIT Message From PS To CUSTOMER> (읽기) |  |  | Function 03 Function 04
| NAME | DESCRIPTION | TYPE | ADDRESS | bit | Range | REMARKS
| PSGP-DI1 | Remote/Local |  | 13 | 0 | 1=Remote, 0=Local
|  | STANDBY |  |  | 1 | 1=READY
|  | POWER ON |  |  | 2 | 1=PULSE ON
|  | Reemote( EXT_Net ) |  |  | 3 | 1 =EXT_Net
|  | Reemote( EXT_Dis ) |  |  | 4 | 1 =EXT_Dis
|  | - reserved - |  |  | 5
|  | WARNING INDICATOR |  |  | 6 | 1=WARNING OCCUR
|  | FAULT INDICATOR |  |  | 7 | 1=FAULT OCCUR
|  | - reserved - |  |  | 8
|  | - reserved - |  |  | 9
|  | - reserved - |  |  | 10
|  | - reserved - |  |  | 11
|  | - reserved - |  |  | 12
|  | - reserved - |  |  | 13
|  | - reserved - |  |  | 14
|  | - reserved - |  |  | 15
| PSGP-DI2 (SPARE-1) | - reserved - |  | 14 | 0~15 | NONE | 항상 0 응답.
| PSGP-DI3 (WARNING) | Warning00-0 : WARNING_EEP_WR_ERR |  | 15 | 0 | 1 = Warning | Fault 발생 시 warning 은 해제됨.
|  | Warning00-1 : WARNING_RS485_CUT |  |  | 1 | 1 = Warning
|  | Warning00-2 : - reserved - |  |  | 2
|  | Warning00-3 : - reserved - |  |  | 3
|  | Warning00-4 : - reserved - |  |  | 4
|  | Warning00-5 : - reserved - |  |  | 5
|  | Warning00-6 : - reserved - |  |  | 6
|  | Warning00-7 : - reserved - |  |  | 7
|  | Warning00-8 : - reserved - |  |  | 8
|  | Warning00-9 : - reserved - |  |  | 9
|  | Warning00-10 : - reserved - |  |  | 10
|  | Warning00-11 : - reserved - |  |  | 11
|  | Warning00-12 : - reserved - |  |  | 12
|  | Warning00-13 : - reserved - |  |  | 13
|  | Warning00-14 : - reserved - |  |  | 14
|  | Warning00-15 : - reserved - |  |  | 15
| PSGP-DI4 (FAULT) | Fault01-0 : FAULT OVER VOLTAGE S/W |  | 16 | 0 | 1= Fault
|  | Fault01-1 : FAULT OVER CURRENT S/W |  |  | 1 | 1= Fault
|  | Fault01-2 : FAULT OVER VOLTAGE HW |  |  | 2 | 1= Fault
|  | Fault01-3 : FAULT OVER CURRENT HW |  |  | 3 | 1= Fault
|  | Fault01-4 : FAULT OVER RESONANT CURRENT |  |  | 4 | 1= Fault
|  | Fault01-5 : FAULT EMERGENCY STOP |  |  | 5 | 1= Fault
|  | Fault01-6 : FAULT OVER SPARK RATE |  |  | 6 | 1= Fault
|  | Fault01-7 : FAULT COMM ERROR |  |  | 7 | 1= Fault
|  | Fault01-8 : FAULT HEATSINK TEMP OVER |  |  | 8 | 1= Fault
|  | Fault01-9 : FAULT 485 CUT |  |  | 9 | 1= Fault ( reserved )
|  | Fault01-10 : FAULT CPU DOWN ERROR |  |  | 10 | 1= Fault
|  | Fault01-11 : FAULT UNDER VOLTAGE |  |  | 11 | 1= Fault
|  | Fault01-12 : - reserved - |  |  | 12
|  | Fault01-13 : - reserved - |  |  | 13
|  | Fault01-14 : - reserved - |  |  | 14
|  | Fault01-15 : - reserved - |  |  | 15
| PSGP-DI5 (FAULT-SPARE1) | - reserved - |  | 17 | 0-15 | NONE | 항상 0 응답.

## PS->Customer(Word)
Technical Document
PROJECT : 10kw 집진기
CUSTOMER :
DOC. Name : 10kw 집진기 Interface List
Power Supply / Customer COMMUNICATION DATA
| <WORD Message From PS To Customer> (읽기) |  |  | Function 03 Function 04
| NAME | DESCRIPTION | TYPE | ADDRESS | Range | Unit | REMARKS
| PS-W5000 | PO | unsigned Int | 18 | 10 | KW | range 제품 메뉴얼 참고
| PS-W5001 | VO | unsigned Int | 19 | 50 | KV | range 제품 메뉴얼 참고
| PS-W5002 | IO | unsigned Int | 20 | 200 | mA
| PS-W5003 | TEMPERATURE | unsigned Int | 21 | 80 | oC
| PS-W5004 | SPARK RATE COUNT | unsigned Int | 22 | 1000 | s/m
| PS-W5005 | Heart Beat | unsigned Int | 23 | 0 ~ 5000 |  | 500us 주기
|  | reserved |  | 24
* address 0번 부터는 func6,16에 쓴 값을 확인 할 수 있음. ( 옵션 )
| PS-W5007 | operationCmd | unsigned Int | 0
| PS-W5008 | OUT POWER | unsigned Int | 1
| PS-W5009 | BASE VOLTAGE | unsigned Int | 2
| PS-W5010 | BASE CURRENT | unsigned Int | 3
| PS-W5011 | SPARK RATE | unsigned Int | 4
| PS-W5012 | QUENCH | unsigned Int | 5
| PS-W5013 | SETBACK | unsigned Int | 6
| PS-W5014 | SETBACK TIME | unsigned Int | 7
| PS-W5015 | UV LEVEL | unsigned Int | 8
| PS-W5016 | UV TIME DELAY | unsigned Int | 9
|  |  |  | 10 ~12 | reserved
( UV = UNDER VOLTAGE )
* range값은 제품과 다를 수 있으니 제품메뉴얼 참고

## Customer->PS(Bit)
Technical Document
PROJECT : 10kw 집진기
CUSTOMER :
DOC. Name : 10kw 집진기 Interface List
Power Supply / Customer COMMUNICATION DATA
| <BIT Message From CUSTOMER To PS> (쓰기) |  |  | Function 06 Function 16
| NAME | DESCRIPTION | TYPE | ADDRESS | bit | Range | REMARKS
| PSGP-DO1 | - reserved - |  | 0 | 0 | - reserved -
|  | FAULT CLEAR |  |  | 1 | 1=CLEAR ( 1 for 2sec )
|  | POWER ON |  |  | 2 | 1=ON , 0 = NO ACTION
|  | POWER OFF |  |  | 3 | 1=OFF , 0 = NO ACTION
4
5
6
7
8
9
|  | * POWER OFF에 '1' 값이 들어와있으면 POWER ON에 '1' 값이 들어와도 ON하지 않음. |  |  | 10
|  | * POWER ON에 '1' 값이 들어와 동작하고 있을 때 POWER OFF에 '1' 값이 들어오면 OFF함. |  |  | 11
12
13
14
15

## Customer->PS(Word)
Technical Document
PROJECT : 10kw 집진기
CUSTOMER :
DOC. Name : 10kw 집진기 Interface List
Power Supply / Customer COMMUNICATION DATA
| <WORD Message From Customer To PS> (쓰기) |  |  | Function 06 Function 16
| NAME | DESCRIPTION | TYPE | ADDRESS | default | Range | Unit | REMARKS
| W6000-PS | OUT POWER | unsigned Int | 1 | - | 0-10.00 | KW | range 제품 메뉴얼 참고
| W6001-PS | BASE VOLTAGE | unsigned Int | 2 | - | 0-50.00 | KV | range 제품 메뉴얼 참고
| W6002-PS | BASE CURRENT | unsigned Int | 3 | 200 | 0-200 | mA
| W6003-PS | SPARK RATE | unsigned Int | 4 | 1000 | 0-1000 | A/m
| W6004-PS | QUENCH | unsigned Int | 5 | 1000 | 4-1000 | ms
| W6005-PS | SETBACK | unsigned Int | 6 | 0.1 | 0.1-20.0 | %
| W6006-PS | SETBACK TIME | unsigned Int | 7 | 1000 | 0-1000 | ms
| W6007-PS | UV LEVEL | unsigned Int | 8 | 10 | 0-20.00 | kV
| W6008-PS | UV TIME DELAY | unsigned Int | 9 | 30 | 0~45 | S
( UV = UNDER VOLTAGE )
* range값은 제품과 다를 수 있으니 제품메뉴얼 참고